SEWER USE ORDINANCE

FOR

TOWN OF MACHIAS, MAINE

March 25, 2000

Amended June 13, 2012

1

Sewer Use Ordinance

Table of Contents

Section	Title	Page

Purpose of the Ordinance	2

100.0	Definitions	2

200.0	Proper Disposal of Sewage Required	7

200.1		Unlawful disposal	7

200.2		Unlawful discharge	8

200.3		Unlawful facilities	8

200.4		Required connections	8

300.0	Private Sewage Disposal	8

300.1	Private subsurface disposal system	8

300.2	Permit required for private system	8

300.3	Required inspections	9

300.4	Operation and maintenance	9

300.5	Additional requirements	9

300.6	Public connection/private system closed	9

300.7	Disposal at treatment plant	9

300.8	Industrial waste disposal	9

400.0	Building Sewers and Connections	9

400.1	Permit required for public system	9

400.2	Classification of sewer permits	10

400.3	Individual sewer hookups	10

400.4	Use of older sewer materials	10

400.5	Sewer specifications	10

400.6	Diameter and slope of sewer	11

400.7	Depth of new sewer	11

400.8	Backfill required	11

400.9	Pumping to municipal line	11

400.10	Excavation requirements	11

400.11	Joints and connections	12

400.12	Connection of building sewer	12

400.13	Inspection notification	12

400.14	Manhole requirements	13

400.15	Excavation barricades	13

400.16	Pressure tolerances	13

400.17	Restrictions of groundwater	13

400.18	Watertight drain covers required	13

Section	Title	Page

400.19	Drain venting	13

400.20	Gravity flow assistance	13

400.21	No connection to force main sewer	14

400.22	In-line water meter required	14

500.0	Sewer Extensions	14

500.1	Sewer extensions described	14

500.2	Extension installed by a developer	14

500.3	Professional engineer designs	15

500.4	Standards for sewer design	15

500.4.1	Pipe material	15

500.4.1.1	Joints	15

500.4.1.2	Internal pipe diameter	15

500.4.1.3	Branch fittings	15

500.4.1.4	Horizontal installation	15

500.4.2	Pipe slope	16

500.4.3	Pipe bedding materials	16

500.4.3.1	Standards for screened stone	16

500.4.3.2	Standards for crushed stone	17

500.4.3.3	Depths of fill	17

500.4.4	Backfill material requirements	17

500.4.4.1	Backfill standards	17

500.4.4.2	Excavation requirements	18

500.4.5	Manhole	18

500.4.5.1	Components of manholes	18

500.4.5.2	Mortar standards	18

500.4.5.3	Manhole steps	18

500.4.5.4	Manhole covers	18

500.4.5.5	Pipe sleeves	19

500.4.5.6	Manhole bases	19

500.4.5.7	Manhole inverts	19

500.4.5.8	Install frames and covers	19

500.4.5.9	Vacuum tests	20

500.5	Sewer main tests	20

500.5.1	Testing described	20

500.5.2	Table of air Test durations	21

500.5.3	Deflection measurements	21

500.6	Non-issuance of permit by developer	22

500.7	Connection to town facilities	22

600.0	Use of Public Sewers	22

600.1	Non connection for groundwater	22

600.2	Storm sewer use	22

600.3	Prohibited discharges	22

Section	Title	Page

600.3.1	Temperature standard	22

600.3.2	Fats, grease, oil contaminants	22

600.3.3	Soluble fats, grease, oil contaminants	23

600.3.4	petroleum-based contaminants	23

600.3.5	Noxious gas contaminants	23

600.3.6	Garbage contaminants	23

600.3.7	Bulk solid contaminants	23

600.3.8	Corrosive contaminants	23

600.3.9	Radioactive contaminants	23

600.3.10	“Slug”	23

600.3.11	Storm water contaminants	24

600.3.12	Toxic contaminant limits	24

600.3.13	Pickling/plating waste contaminants	25

600.3.14	Phenols contaminants	25

600.3.15	Untreatable contaminants	25

600.3.16	Biological process inhibiter contaminants	25

600.3.17	Dissolved solids, dye contaminants	25

600.3.18	Inert/organic suspended solids	25

600.3.19	Increased toxicity contaminants	25

600.3.20	Boiler blow-off contaminants	25

600.3.21	Septage process discharge	25

600.4	BOD standards	26

600.5	Standards for water characteristics	26

600.6	Individualized agreements	26

600.7	Application of standards	26

600.8	Town options for illegal dumping	27

600.8.1	Rejection of materials	27

600.8.2	Required pre-treatment	27

600.8.3	Quantities and rates of discharge	27

600.8.4	Payments	27

700.0	Pretreatment and Permitting of

Industrial and Unusual Wastes	27

700.1	Industrial use of sewage system	27

700.1.1	No federal violations	27

700.1.2	No upset to plant processes	27

700.1.3	No untreatable materials	28

700.1.4	No contaminated materials	28

700.1.5	No creation of hazardous conditions	28

700.1.6	Equitable allocation of fees	28

700.2	Owner provided equalizers	28

700.3	Suitable control devices	28

700.4	No diluting discharges	28

700.5	Grease, oil, sand interceptors	29

Section	Title	Page

700.6	Interceptors maintenance	29

700.7	Categorical pretreatment standards	29

700.8	Local limits	29

700.9	Waster water surveys	29

700.9.1	Survey form identification	30

700.9.2	SIC code of user	30

700.9.3	Waste water constituents	30

700.9.4	Time and duration of discharges	30

700.9.5	Flow rates	30

700.9.6	User premise plan	30

700.9.7	Discharge materials	30

700.9.8	Prohibited materials nature/concentration	31

700.9.9	Product identification	31

700.10	Signed disclosure forms	31

700.11	Additional information	31

700.12	Discharge permit required	32

700.13	Conditions for permits	32

700.14	Length of discharge permit	32

700.15	Specificity of permit	32

700.16	Permit specifications	33

700.17	Waste water discharge parameters	33

700.18	Installation requirements	33

700.19	Town modifications of permits	33

700.20	Advance notice	33

700.21	Hazardous waste discharge/slug control plan	33

700.21.1	Description of discharge practices	33

700.21.2	Stored chemicals	33

700.21.3	Notifications for accidental discharges	33

700.21.4	Procedures to prevent accidental discharges	34

700.21.5	Notification of Plant Operator	34

700.22	Schedule of additional pretreatment, operations

or maintenance	34

700.23	Reports from significant industrial users	34

700.24	Notification of changes	35

700.25	Violations found though sampling	35

800.0	Ordinance Compliance Monitoring	36

800.1	LPI Right of Entry	36

800.2	Entry via easements	36

800.3	User bears costs of sampling	36

800.4	Monitoring equipment	37

800.5	Record keeping	37

800.6	Public inspection of records	37

800.7	Administrative inspection warrant	38

Section	Title	Page

900.0	Protection from damage	38

900.1	Willful damage	38

900.2	Certificate of Insurance requirement	38

1000.0	Sewer charges	38

1000.1	Sewer service charges	38

1000.2	Board of Selectman sets fees	39

1000.3	Special sewer charge	39

1000.4	Interest charged	39

1100.0	Enforcement	39

1100.1	Nuisances	39

1100.2	Notification	39

1100.3	Legal action	40

1100.4	Penalty	40

1200.0	Conflict with other ordinances	40

1300.0	Severability	41

The purpose of this Ordinance is to promote the health and general welfare of the citizens of the Town of Machias by regulating and restricting the construction and use of sewerage systems and the accumulation, transportation, treatment and disposal of sewage in such a manner that the creation of any sewerage system, whether public, private, or industrial, shall not result in pollution, health hazard, or other nuisance. Hereafter, any person owning any building or structure with in the town of Machias which is the source of sewage and/or industrial wastes, or who proposes to erect such building or structure, shall conform to the requirements of this Ordinance.

SECTION 100.0 – DEFINITIONS

“BOD” (denoting Biochemical Oxygen Demand) shall mean the quantity 		of oxygen utilized in the biochemical oxidation of organic matter in five		(5) days at 20 degrees C, expressed in milligrams per liter, as determined		by test methods defined in Standard Methods.

“Building Drain” shall mean that part of the lowest horizontal piping of a		drainage system which receives the discharge from soil, waste, and other		drainage pipes inside the walls of the building and conveys it to the			building sewer, beginning eight (8) feet outside the inner face of the 		building wall.

“Building Sewer” shall mean the extension from the building drain to the		public sewer or other place of disposal.

“Categorical User” shall mean any user of the Town’s waste water		treatment system whose dischargers are regulated under 40 CFR Part 403 		and 40 CFR Parts 405-471, or who is otherwise subject to U.S. EPA pre-		treatment requirements as a categorical user.

“Chlorine Demand” shall mean the amount of chlorine required to 		destroy all pathogenic organisms present and oxidize all organic, inorganic		and ammonia-based compounds in a sewage stream.

“Town” shall mean the Town of Machias acting through its Selectmen, 		manager, superintendent, plant operator, employees, code enforcement		officer, plumbing inspector, or other duly authorized agent.

“Selectmen” shall mean the duly elected Board of Selectmen of the Town 		of Machias.

“Combined Sewer” shall mean a sewer receiving both surface runoff and		sewage.

2

SECTION 100.0 – DEFINITIONS – continued

“Developer” shall mean any person or persons who undertake to construct 		simultaneously, or in planned sequence, more than one housing unit on a 		given tract or land subdivision, or other land development which is to be		connected to the Municipal Sewer System.

“Engineer” shall mean a Professional Engineer retained as Town 			Engineer or Consulting Engineer and retained or appointed by the 		Machias Town Manager.

“Excessive” shall mean masses or concentrations of a constituent in a

Sanitary or industrial waste water which, in the judgment of the Town:

(a) will cause damage to any facility, (b) will be harmful to any waste		water treatment process, (c) cannot be properly removed in the Town’s		treatment facilities, (d) may inhibit the final disposal or reuse of the 		treatment plant’s sludge residuals, (e) can otherwise endanger life or 		property, or (f) can constitute a nuisance.

“Garbage” shall mean solid wastes from the domestic and commercial		preparation, cooking, and dispensing of food, and from the handling, 		storage, and sale of produce.

“Industrial user” shall mean a person who discharges industrial waste		to the POTW of the Town.

“Industrial Wastes” shall mean the liquid or solid wastes from industrial		manufacturing processes, trade, or business as distinct from sanitary 		waste water. Industrial wastes may or may not be discharged separately		from sanitary waste waters. For a combined discharge, the Town shall 		determine if the discharge meets the definition of “industrial wastes”.

“Interference” shall mean a discharge, which alone or in conjunction		with a discharge or discharges from other sources,  inhibits or disrupts the		sewage works, its treatment processes or operations or its sludge 			processes, use or disposal; and therefore is a cause of a violation of the		Town’s NPDES permit or of the prevention of sewage sludge use or		disposal in compliance with any of the following statutory/regulatory pro-		visions or permits issued there under, or any more stringent State or local		regulations: Section 405 of the act;  the Solid Waste Disposal Act, 			including Title II commonly referred to as RCRA; any State regulations		contained in any State sludge management plan prepared pursuant to 		Subtitle D of  the Solid Waste Disposal Act; the clean Air Act; the Toxics

Substances Control Act; the Marine Protection, Research, and Sanctuaries		Act; 40 CFR Part 503 Standards for Sewage Sludge Use and Disposal and

RSA 485-A: 4, XVI-a.

3

SECTION 100.0 – DEFINITIONS – continued

“National Pollutant Discharge Elimination System Permit or NPDES 		Permit” shall mean a permit issued to the Town pursuant to Section 402 		of the Act (33 U.S.C. 1342).

“Natural Outlet” shall mean any outlet into a watercourse, pond, ditch,		lake, or other body of surface or groundwater.

“Objectionable Waste” shall mean waste that has the demonstrated		potential to adversely affect public health or pollute ground and/or 			surface water.

“Owner” shall mean both the person who is the vested holder of title for		any real estate and all tenants, lessees, or others in control or use of the		property in question. Excluded from this definition is a mortgagee of the		property in question unless the mortgagee exercises his mortgage rights 		and becomes an owner.

“Pass Through” shall mean a discharge that exits the sewage works into		waters of the United States in quantities or concentrations that, alone or in		conjunction with a discharge or discharges from other sources, is a cause 		of a violation of any requirement of the Town’s NPDES permit, including		an increase in the magnitude or duration of a violation.

“Person” shall mean any individual, firm, company, association, partner-		ship, society, corporation, or group.

“PH” shall mean the logarithm of the reciprocal of the weight of hydrogen		ions in grams per liter of solution.

“Plant Operator” shall mean the Superintendent or operator of the Town 		facilities, or his authorized deputy, agent, or representative, all acting for 		the Town Selectmen.

“Plumbing Inspector” shall mean the Plumbing Inspector of the Town 		Of Machias, Maine.

“Pretreatment” shall be the reduction of the amount of pollutants, the		elimination of pollutants, or the alteration of the nature of pollutant pro-		perties in waste water prior to, or in lieu of, introducing such pollutants 		into the sewage works. This reduction or alteration can be obtained by 		physical, chemical, or biological processes; by process changes; or by		other means, except by diluting the concentration of pollutants unless		allowed by the applicable pretreatment standard.

4

SECTION 100.0 – DEFINITIONS – continued

“Pretreatment Requirements” shall be any substantive or procedural

requirement related to pretreatment imposed on the user, other than

pretreatment standard.

“Pretreatment standard or standards” shall mean prohibited 		discharge standards, (categorical pretreatment standards), and local limits.

“Private Sewer Systems” shall mean any sewer that collects waste		water from two or more building sewers, owned separately, and 		discharging to a public sanitary sewer. Private sewer systems are not		permitted except by specific agreement with the Town.

“Properly Shredded Garbage” shall mean the wastes from the 			preparation, cooking, and dispensing of food that has been shredded to		such a degree that all particles will be carried freely under the flow			conditions normally prevailing in public sewers, with no particle 			greater than one-half (1/2) inch in any dimension.

“Public Sewer” shall mean a sewer in which all owners of abutting 			properties have equal rights, and is owned by the Town.

“Sanitary Sewer” shall mean a sewer which carries sewage and to which		storm, surface, and ground waters are not intentionally admitted.

“Septage” shall mean the mixture of liquids and solid matters removed 		from septic tanks during normal cleaning.

“Sanitary Waste Water” shall mean the liquid waste discharge from a 		building’s or structure’s sanitary fixtures, such as toilets, washrooms, 		urinals, sinks, showers, small laundries, and from kitchens and cafeterias		essentially free of industrial wastes or toxic materials. Sanitary waste 		water may or may not be discharged separately from industrial waste 		water. For a combined discharge the Town shall determine if a waste		water discharge meets the definition “sanitary waste water”.

“Sewage” (sometimes termed “Waste water” or “waste”) shall mean a		combination of the water carried wastes from residences, business			buildings, institutions and industrial establishments, together with such		ground, surface, and storm water as may be present.

“Sewage Treatment Plant or Water Pollution Control Plant” shall mean 		any arrangement of devices and structures used for treating sewage and 		industrial waste.

5

SECTION 100.0 – DEFINITIONS – continued

“Sewage Works” shall mean all municipal facilities for collecting, 			pumping, treating and disposing of sewage.

“Sewer” shall mean a pipe or conduct for carrying sewage.

“Shall” is mandatory: “May” is permissive.

“Significant Industrial User” shall mean a user subject to categorical		pretreatment standards; or a user that (a) discharges an average of 10,000		gpd or more of process waste water to the sewage works, excluding 		sanitary, non-contact cooling, and boiler blow down waste water; or (b)		contributing a process waste stream which makes up two percent (2%) of		more of the average dry weather hydraulic or organic capacity of the 		sewage works; or (c) is designated as such by the  Town on the basis that		it has a reasonable potential for adversely affecting the sewage works.

“Significant Non-compliance or SNC” shall mean that an industrial		user is in significant non-compliance if its violation meets one or more of		the following criteria:

a.) Chronic Violations – A pattern of violating the same pretreatment		standard daily maximum or average limit (any magnitude or limit) sixty		six percent (66%) or more of the time in a 6 month period.

b.) Technical Review Criteria (TRC violations) – Thirty three percent 		(33%) or more of the measurements exceed the same pretreatment 			standard daily maximum limit or average limit by more than the TRC 		factor in a six month period. The TRC factor is 1.4 for biochemical			oxygen demand (BOD), total suspended solids (TSS), oil & grease and 1.2		for all other pollutants except pH;

c.) Any other discharge violation that the Plant Operator believes has 		caused, alone or in combination with other discharges, interference or 		pass through, including endangering the health of sewage works personnel		or the general public;

d.) Any discharge of pollutants that has caused imminent endangerment to 	the public or to the environment, or has resulted in the Plant Operator’s		exercise of its emergency authority to halt or prevent such a discharge;

e.) Failure to meet, within ninety (90) days of the scheduled date, a 		compliance schedule milestone contained in a waste water discharge 		permit or enforcement order for starting construction, completing 			construction, or attaining final compliance;

6

SECTION 100.0 – DEFINITIONS – continued

f.) Failure to provide within thirty (30) days after the date, any required		reports, including baseline monitoring reports, Industrial Discharge Permit		Applications, reports on compliance with categorical pretreatment 			standard deadlines, periodic self monitoring reports, and reports on 		compliance with compliance schedules;						        					g.) Failure to accurately report non-compliance; or

h.) Any other violation that the Plant Operator determines will adversely		affect the operation or implementation of the local pretreatment standards.							“Slug” shall mean any discharge of water or waste water in which the 		rate of discharge, or the mass or concentration of any given constituent 		exceeds, in the opinion of the Town, the ability of the sewage works to 		function efficiently or properly.										“Standard Methods” shall mean Standard Methods for the Examination of		Water and Waste water, latest edition.

“Storm Drain” (sometimes termed “storm sewer”) shall mean a sewer			which carries storm and surface waters and drainage, and/or non-				contaminated cooling water, but excludes sewage and industrial wastes.

“Superintendent” shall mean the superintendent of public works and/or			superintendent of the sewage works of the Town of Machias, or their			authorized representative.																					“Suspended Solids” (also called “Total Suspended Solids”) shall mean			solids that either float on the surface of, or are in suspension in, water, 			sewage, or other liquids, and which are determined in accordance with			Standard Methods.																						“Watercourse” shall mean a channel in which flow of water occurs, either			continuously or intermittently.

SECTION 200.0 – PROPER DISPOSAL OF SEWAGE REQUIRED

200.1   It shall be unlawful for any person to place, deposit, or permit to be deposited in 	any unsanitary manner on public or private property within the Town of Machias, 		or in any area under jurisdiction of said Town, any human or animal excrement, 		greywater, garbage, sewage or other objectionable waste. The term “Unsanitary		manner” shall not include reasonable spreading of animal excrement or other

7

SECTION 200.0 – PROPER DISPOSAL OF SEWAGE REQUIRED – continued

200.1 continued

Fertilizer in farming or animal husbandry operations or septage disposed of at a 		septage site licensed by the State of Maine Department of Environmental			Protection and operated in compliance with all State of Maine Department of 		Environmental Protection site regulations.

200.2 	It shall be unlawful to discharge to any natural outlet within the Town of Machias,		or in any area under the jurisdiction of said Town, any sewage or other polluted		waters, except where suitable treatment has been provided in accordance with 		subsequent provisions of this Ordinance and the requirements of the State of		Maine.

200.3	It shall be unlawful to construct or maintain any privy, privy vault, septic tank,		cesspool, or other facility intended or used for the disposal of sewage, except		where no public sewage facilities are available. Said systems shall be in 			compliance with the State of Maine Subsurface Wastewater Disposal Rules.

200.4 	Except as herein provided, the owner of all houses, buildings, or properties us for human occupancy, employment, recreation, or other purposes requiring the disposal of sewage situated within the Town and abutting on any street, alley, or right of way in which there is located a public sanitary sewer of the Town is hereby 	required at his expense to install suitable toilet facilities therein, and to connect such facilities directly with the proper public sewer in accordance with then provisions of this Ordinance, provided that said public sewer is within two hundred (200) feet of the structure containing internal plumbing.

SECTION 300.0 – PRIVATE SEWAGE DISPOSAL

300.1	Where a public sanitary sewer is not available the building sewer shall be 			connected to a private disposal system complying with the requirements of the		State of Maine Plumbing Code, Part II, Subsurface Wastewater Disposal Rules 		and/or Town Ordinances as from time to time amended. An approved private		subsurface wastewater disposal system may continue to operate and be utilized		until said system fails or malfunctions.

300.2	Before commencement of construction of a private sewage disposal system, the		owner shall first obtain a written permit signed by the Plumbing Inspector. The		application for such permit shall be made on a form furnished by the Town, 		which the applicant shall supplement by any plans, specifications, and other 		information as are deemed necessary by the Plumbing Inspector. A permit and		inspection fee shall be paid in advance at the time the application is filed. The		amount of this fee shall be set by the Town Selectmen.

8

SECTION 300.0 – PRIVATE SEWAGE DISPOSAL – continued

300.3	A permit for a private sewage disposal system shall not become effective until the 	installation is completed to the satisfaction of the Plumbing Inspector. He shall be		allowed to inspect the work at any stage of construction and, in any event, the		applicant for the permit shall notify the Plumbing Inspector when the work is 		ready for final inspection, and before any underground portions are covered. The		inspection shall be made within twenty four (24) hours of the receipt of notice by		the Plumbing Inspector.

300.4	The owner shall operate and maintain the private sewage disposal facilities in a 		sanitary manner at all times in accordance with the State of Maine Subsurface		Wastewater Disposal rules, regulations and laws.

300.5	No statement contained in this section shall be construed to interfere with any		additional requirements that may be imposed by the Town.

300.6	When a public sewer becomes available, the building sewer may continue to utilize a private subsurface wastewater disposal system until for a period of up to twelve (12) months after the date the public sewer is installed. After this time period, the building will be required to be connected to said public sewer forthwith and the private septic tank and/or cess pool shall be cleaned of sludge and filled with clean bankrun gravel or dirt, or otherwise made to comply with State law, rules and regulations.

300.7	The contents from septic tanks of Machias properties may be discharged to	 the sewage treatment plant upon approval from the superintendent of the plant or agent. A fee shall be paid to the Town prior to discharge. The amount of the fee shall be set by the Town Selectmen.

  - There shall be no discharge of industrial waste to the Machias River or any

water body unless the discharging party affirmatively proves to the Town’s

reasonable satisfaction that the proposed industrial waste discharge will, at

all times, meet the State of Maine Department of Environmental Protection

and United States Environmental Protection Agency discharge standards applicable to the Machias Wastewater Treatment facility as from time to time established.

SECTION 400.0 – BUILDING SEWERS AND CONNECTIONS

400.1	No unauthorized person shall uncover, make any connections with or opening	 into, use, alter, or disturb any public sewer or appurtenance thereof without first

obtaining a written permit from the Town or authori	zed representative.  All work

related to the installation of building sewers and the connection  to the public

sewer shall be performed by persons qualified in this class of work and acceptable

9

SECTION 400.0 – BUILDING SEWERS AND CONNECTIONS – continued

400.1 –continued

to the Town of Machias. Said work shall be completed in compliance with all

Municipal Ordinances and State of Maine Laws and Regulations with inspection

by the Town for compliance. Failure to comply with inspection provisions may

result in excavating the installation for inspection.

  - There shall be two (2) classes of building sewer permits: (a) for residential and

commercial service, and (b) for service to establishments producing industrial

wastes. In either case, the owner or his agent shall make application on a special

form furnished by the Town. This permit application shall be supplemented by

any plans, specifications, or other information considered pertinent in the		 judgment of the Town. A fee for a connection and inspection permit for a sewer	 entrance to the Town sewer shall be paid to the Town prior to connection to the	 Town sewer. The amount of said fee shall be as from time to time established by 	 the Town of Machias Selectmen.

In the case of multiple building units or connections, connections involving sewer	 extensions, or industrial discharge or pretreatment applications, the Town may 	 require a monetary deposit sufficient to cover the cost of review of the 		 application, including any expert advice deemed necessary by the Town. The 	 amount of deposit shall be estimated by the Town and upon payment by the 	 applicant kept in an account. Upon completion the review process, the unused	 portion, if any, will be refunded. If the initial deposit is not sufficient to pay for	 the costs incurred by the Town, a second deposit shall be made and handled in the	 same manner as the first.

400.3	A separate and independent sewer shall be provided for every building; except 	 where one building stands at the rear of another on an interior lot and no private	 sewer is available or can be constructed to the rear building through an adjoining 	 alley, courtyard, or driveway, the building sewer from the front building may be	 extended to the rear building and the whole considered as one building sewer 	 except for the purposes of Section 1000 and if approved by the Town.

400.4	Old building sewers may be used in connection with new buildings only when 	 they are demonstrated by the owner to the Town’s reasonable satisfaction to be 	 adequate to meet the requirements of this Ordinance.

400.5	Except as herein provided, the building sewer shall meet one of the following	 specifications: 1) PVC Sewer SDR 35 – ASTM D3034, 12 ½ foot or 20 foot 	 lengths, neoprene ring lock in, maximum allowable deflection – 5.0 percent;

10

SECTION 400.0 – BUILDING SEWERS AND CONNECTIONS – continued

400.5 – continued

2) PVC water pipe Class 200, SDR-21, for maximum 2 inch diameter pressure	 service, 20 foot lengths ASTM-D2241 and D3139, neoprene ring in grooved	 bell, maximum allowable deflection – 5.0 percent; 3) Extra heavy cast iron soil	 pipe ASTM-A74, rubber ring in grooved bell, ASTM-C564; or 4) Ductile iron 	 push on joint sewer pipe, Class 51, ASTM-A746, 18 foot or 20 foot lengths. For	 building sewers over 100 feet in length from the interior building wall to the	 connection point to the public sewer, the minimum inside pipe diameter shall be	 six (6) inches. In addition, a vertical pipe clean out to grade shall be installed 	 every 100 feet, said clean out shall be the same size as the sewer line.

400.6 	The diameter of the building sewer shall not be less than four (4) inches nor shall

the slope of the pipe be less than one quarter (1/4) inch per foot.

400.7	The depth of new building sewers shall be sufficient to afford protection from frost as determined by the Town, but in no event shall be less than five (5) feet to the crown of the pipe unless properly insulated at shallower depths. The building sewer shall be laid at uniform grade and in straight alignment in so far as possible. Changes in direction shall be made only at a manhole or with properly curved pipe and fittings with a vertical clean out to grade. The ends of building sewers, which are not connected to the building drain of the structure for any reason, shall be sealed against infiltration by a suitable stopper, plug, or other approved means.

400.8	Backfill: Whenever insulation is required for frost protection, the sewer line shall be covered with a minimum of two (2) inches of compacted sand upon which the appropriate insulation (insulation appropriate to afford adequate frost protection) shall be placed, and said insulation shall be covered with a minimum six (6) inches of sand. The remaining backfill as required in Section 400.1.

400.9	In all buildings in which any building drain is too low to permit gravity flow to the public sewer, sewage or industrial wastes carried by such drain shall be lifted by mechanical means, as approved by the Town, and discharged to the building sewer at owner’s expense.

400.10 All excavation required for the installation of a building sewer shall be open trench work unless otherwise approved by the Town. The building sewer shall be laid on a mix inch bed of firm half (1/2) inch to one (1) inch crushed stone or gravel and back filled by hand with same crushed stone or gravel. The hand fill shall be placed around the pipe and over it to a compacted depth of at least six (6) inches over the pipe. Backfill up to six (6) inches over the pipe shall be tamped. The remainder of the trench may be back filled by machine with no stone greater than three (3) inches. Reconstruction of pavement surface, including gravel base

11

SECTION 400.0 – BUILDING SEWERS AND CONNECTIONS – continued

400.10 continued

courses, shall be in accordance with Maine Department of Transportation and Town of Machias specifications and Ordinances as appropriate. Pipe laying and backfill shall be performed in accordance with Section 3 through 6 of ASTM Specification C12. No backfill shall be placed until the work has been inspected.

400.11 All joints and connections shall be made gas tight and water tight with approved gaskets, Fernco couplings or equal. The transition joint between pipes of different materials shall be made with adapters and joint materials approved by the Town. Pre-molded gasket joints shall be used and shall be neoprene compression type gaskets which provide positive double seal in the assembled joint. The gasket shall be a pre-molded one piece unit designed for joining the pipe material used. The assembled joint shall be sealed by compression of the gasket between the exterior surface of the spigot and the interior surface of the hub. The joint shall be assembled following the manufacturer’s recommendation using acceptable lubricant and special pipe coupling tools designed for that purpose. Lubricant shall be a bland, flax base, non-toxic material, and shall not chemically attack the gasket material.

400.12	The connection of the building sewer into an existing public sewer shall be made at the existing public sewer. All costs and expense incidental to the installation and connection of the entire length of building sewer shall be borne by the owner. The owner shall indemnify the Town from any loss or damage that may directly or indirectly be occasioned by the installation of the building sewer. The method of connection of the building sewer to the public sewer will be dependent upon the type of pipe material used and in all cases shall be approved by the Town. The connection of the building sewer into the public sewer shall be made with a wye or tee branch. If none is available, a connection may be made by tapping the existing sewer with a saddle by a method approved by the Town.

400.13	The applicant for the building sewer permit shall notify the Town at least forty eight (48) hours prior to when the building sewer is ready for inspection, testing, and connection to the public sewer. The testing and connection shall be made under the supervision of the Town.

When trenches are opened for the laying of building sewer pipes, such trenches shall be inspected by the Town before the trenches are filled, and the person performing such work shall notify the Town when the installation of the building sewer is completed. If the trench is filled before inspection, the Town may require it to be re-excavated for inspection.

12

SECTION 400.0 – BUILDING SEWERS AND CONNECTIONS – continued

400.14	When any building sewer is to serve a school, hospital, or similar institution, or is to serve a complex of industrial or commercial buildings, or which, in the opinion of the Town, will receive sewage or industrial wastes of such rate, volume, or character that frequent maintenance of said building sewer is anticipated, then such building sewer shall be connected to the public sewer through a manhole. The Town shall determine if and where this type of connection to the public sewer is required. Connections to existing manhole shall be made as directed by the Town. If required, a new manhole shall be installed in the public sewer pursuant to Section 500 and 700 and the building sewer connection made there to as directed by the Town.

400.15	All excavations for building sewer installation shall be adequately guarded with barricades and lights so as to protect the public from hazard. Streets, sidewalks, parkways, and other public property disturbed in the course of the work shall be restored in a manner satisfactory to the Town.

400.16	All parts of new building drains and sewers shall withstand, under test without observable leakage, a ten foot head of water for a minimum period of fifteen minutes at a temperature above the freezing point of water.

400.17	No persons shall make connections of roof drains, downspouts, foundation drains, areaway drains, basement drains, sump pumps, or other sources of surface runoff or groundwater, to a building sewer or building drain which in turn is connected directly or indirectly to a public sanitary sewer.

400.18	The covers of all building drains and building sewer manholes, inspection chambers, clean outs, and the like shall be watertight and shall be capable of withstanding, without damage or displacement, any traffic loads to which they may be subject.

400.19	The building drain system shall be so vented that under no circumstances will the seal of any appliance be subjected to a pressure differential in excess of one (1) inch of water. All appliances connected directly or indirectly to the building drain shall have traps with a liquid seal not less than two (2) inches in depth.

400.20	Whenever practical, the building sewer pipe shall be brought to the building drain at an elevation below the basement floor. In all buildings in which any building drain is too low to permit gravity flow to the public sewer, wastewater carried by such building drain shall be lifted by an approved mans and discharged to the building sewer or service lateral. Plans and details of the proposed method shall be submitted to the Town for review.

13

SECTION 400.0 – BUILDING SEWERS AND CONNECTIONS – continued

400.21	No connection of any kind shall be made directly from any private property to a Town pressurized force main sewer.

400.22	All connections made to the public sanitary sewer from a building utilizing a groundwater well water supply shall be required to install an in-line water meter supplied, installed, and maintained by the Town for the purposes of sewer billing. Cost of said installation shall be paid in advance to the Town, with maintenance costs to be billed with the sewer bill.

SECTION 500.0 – SEWER EXTENSIONS

500.1	Sewer extensions, including individual building sewers from the sewer to the property line, or the right of way bound road may be constructed by the Town under public contract if, in the opinion of the Selectmen, the number of properties to be served by such extension warrants its cost and/or this extension is deemed by the Selectmen to be in the public (versus private) interest and if the treatment plant has the capacity to handle said extension. Unless the Town agrees to pay, the property owner shall pay for and install the building sewer from the public sewer to his residence or place of business in accordance with the requirements of this ordinance including but not necessarily limited to Section 400.0. Property owners may propose sewer extensions within the Town by drafting a written petition, signed by a majority of the benefiting property owners, and filing it with the Town. The cost of such extensions may be assessed to the benefited property owners in accordance with State Statutes and/or local ordinance.

500.2	If the Town does not elect to construct a sewer extension at public expense, the property owner, builder or developer may construct the necessary sewer extension, if such extension is approved by the Selectmen in accordance with the requirements of this section. He or they must pay for entire extension, including all expenses incidental thereto. If the Selectmen determine it to be in the public’s interest, a cost sharing agreement between property owner, builder, or developer and the Town may be mutually agreed upon. Each building sewer must be installed and inspected as previously required and the connection fee shall be paid. Design of sewers shall be as specified in this section. The installation of the sewer extension may be subject to such inspection as the Town deems necessary and the expenses for such inspections shall be paid for by the owner, builder or developer prior to connection to the Town sewer. The Town’s decisions shall be final in the matters of quality and methods of construction. The sewer, as constructed, must pass all tests required in this section before it is to be used. Except in instances where mutual agreement for cost sharing as has been mentioned above, the cost of sewer extensions thus made shall be paid by the developers or the property owners, including the costs of all building sewers.

14

SECTION 500.0 – SEWER EXTENSIONS

500.3	All extensions to the sanitary sewer system shall be designed by a Professional Engineer registered in the State of Maine. Plans and specifications for sewer extensions shall be submitted to the Town forty five (45) days before the regularly scheduled Selectmen’s meeting at which Town approval of the extension will be required. The expenses incurred by the Town in reviewing the plans and specifications shall be paid from a deposit made by the owner, builder, or developer at the time of application. The design of sewers and pump stations to be deeded to the Town shall anticipate and allow for flows from possible future system extensions or developments within the future drainage areas.

500.4	Sewer design shall be in accordance with the following:

500.4.1 	Pipe material shall be PVC made from virgin plastic conforming to 					ASTM D 1784, Type 1, Grade 1, and manufactured in accordance with					ASTM D 3034, SDR 35 or ASTM F 789, ductile iron conforming to 					ANSI Specification A 21.51, with iron Grade 60-42-10, and cement					lining meeting ANSI Specification A 21.4, but twice the thickness 					specified; or other material approved by the Town.

500.4.1.1	All joints shall be prepared and installed in accordance with the 					manufacturer’s recommendations, and shall be gastight and water-					tight. Joint materials shall be as follows:										1. PVC – ASTM D 3212

2. Ductile Iron – ANSI  Specification A 21.11.

500.4.1.2	Minimum internal pipe diameter shall be eight (8) inches.

500.4.1.3	Branch fittings for house services shall be PVC wyes or tee-wyes, or					ductile iron saddles with stainless steel straps and “O-ring” seal set in					mastic to create a watertight connection.

500.4.1.4	Sanitary Sewers shall be laid at least 10 feet horizontally from any 					existing or proposed water main, per State of Maine Department of					Human Services Regulations. The distance shall be measured edge of					pipe to edge of pipe. At crossings, one full length of sewer pipe shall 					be located so both joints will be as far from the water pipe as possible.					Special structural support for the water and sewer pipes may be 					required.

15

SECTION 500.0 – SEWER EXTENSIONS – continued

500.4.2 	Minimum slope of sewer pipe shall be as follows:

Minimum Slope in Feet

Pipe Diameter	          Per 100 Feet

8 inch			0.40					   10 inch			0.28					   12 inch			0.22					   14 inch			0.17					   15 inch			0.15					   16 inch			0.14

500.4.3	The pipe shall be bedded with crushed or screened stone from 6” below the pipe to 6” above the pipe. The trench shall be excavated to the required grade and 6”	 of bedding installed and compacted. The pipe shall be installed on the bedding and the joints assembled in accordance with the recommendations of the manufacturer. Bedding material shall then be installed to the mid point of the pipe. The bedding shall be worked and packed under the edges of the pipe with hand shovels and then it shall be compacted. Bedding material shall then be installed to 6” above the pipe and compacted.

All compacting of bedding material shall be done with a vibrating plate compactor for the full trench width. Care shall be taken to prevent movement of the pipe during bedding installation, compacting, and back filling.

Blocking (installation of the pipe prior to bedding and then support of the pipe while bedding is installed under it) shall not be allowed.

All field cutting and beveling of pipe shall comply with the manufacturer’s recommendations. Ends shall be cut square and perpendicular to the pipe axis. Ends shall be beveled, filed smooth and stop marked with a felt tip marker so that they are comparable to factory pipe spigots.

500.4.3.1	SCREENED STONE – Screened stone shall consist of clean, hard, 				durable stone particles. It shall be screened and contain uniformly 				graded stone particles ranging in size from 10 to 20mm unless other-				wise specified. Screened stone shall be free of fine gravel, sand, dirt,				vegetation, disintegrated or laminated soils, and other unsuitable				material.

16

SECTION 500.0 – SEWER EXTENSIONS – continued

500.4.3.2	CRUSHED STONE – Crushed stone shall consist of clean, hard, 				durable stone fragments. It shall be crushed and contain uniformly 				graded stone fragments ranging in size from 20 to 30mm unless other-				wise specified. Crushed stone shall be free of fine gravel, sand, dirt,				vegetation, disintegrated or laminated soils and other unsuitable 				material.

500.4.3.3	Crushed or screened stone shall be placed in lifts which will compact 				to a 6” maximum layer. Gravel and borrow shall be placed in 8” 				maximum lifts. All placement and compacting of borrow and bedding				shall comply with Section 500.4.4 Backfilling.

500.4.4	Backfill material shall then be placed and compacted. Generally the excavated 		soil shall be suitable as backfill and shall be replaced in the excavation. 			Exceptions, include frozen fill, fill containing large stones, stumps or other 		rubble, and any material deemed unsuitable by the Town.

500.4.4.1	Backfilling shall proceed as soon as possible after underground con-				struction has been completed. Backfill shall be extended to the grade				indicated on the plans, compacted and graded.

Fill material shall be placed in layers not to exceed 8” and compacted				to a density equal to at least 95% of the optimum density determined 				by the modified proctor test. Compacting may be done by vibrating				compactor or roller.

The Contractor shall take care not to damage or disturb any structure,				including his own, during backfilling and compacting. The Contractor				shall be held liable for any such damage.

Excavations in paved areas shall be paved according to specifications				as soon as possible. Other areas shall be loamed and seeded or other-				wise restored to a condition equal to or better than that of adjacent 				areas as soon as possible.

The Contractor shall not withdraw any sheeting without the approval	 	of the Town. All voids created by such removal shall be filled and 		compacted. Any backfilling which does not conform to these

17

SECTION 500.0 – SEWER EXTENSIONS – continued

500.4.4.1- continued

Specifications, or which settles differentially, shall be excavated to a				depth sufficient to correct the problem and re-filled as required. Any 				pavement or structure which is damaged due to settlement of backfill				shall be repaired by the Contractor at his expense.

500.4.4.2	All excavations required for the installation of sewer extensions shall 				be open trench work unless approved by the Town. No backfill shall 				be placed until the work has been inspected by the Town.

500.4.5	Manholes shall be constructed at the end of all lines, at all changes in slope or 		alignment or at intervals not exceeding 400 linear feet, unless acceptable to the		Town and shall be pre-cast concrete.

500.4.5.1 	All manholes shall be constructed of pre-cast concrete. Manholes shall				be designed for H-20 loading. Concrete manholes shall have 4000 psi				28 day strength (for 4’ dia and 5000 psi for any of larger dia.) and shall				acquire 75% of their 28 day strength before being shipped to the 				project. Manholes shall have factory cast holes at the proper location 				and elevation as shown on the contract drawings. Manhole sections 				shall be joined with butyl rubber kent seal no. 2. Minimum thickness 				of the reinforced barrel sections and base shall be 5 inches. All man-				holes shall be eccentric cones. The tops of the cones shall be 8 inches 				wide to accommodate bricks. Two coats of bituminous waterproofing				shall be applied to the outside of all manholes. Damaged manholes 				shall be rejected.

500.4.5.2	Mortar to be used in the construction of inverts and placement of 				frames shall be Type II Portland cement (1 Part), sand (2 parts) and 				hydrated line (not over 10 lbs. per bag of cement). Bricks shall be solid				red clay bricks, not concrete units.

500.4.5.3	Manhole steps shall be polypropylene plastic coated steel by M.A. 				Industries or approved equal. Steps shall be cast into the manhole				sections and spaced a maximum of 12” on center vertically.

500.4.5.4	Covers shall be 24” diameter and shall be clearly marked “SEWER”.				Frames shall have a clear opening of 22”. The castings shall be of 				good quality even grained gray cast iron (ASTM-A48 Grade 30) and				shall be free of lumps, blisters, scales, and other defects. Manhole 				covers shall have two lift holes and shall be matched to the frames

18

SECTION 500.0 – SEWER EXTENSIONS – continued

500.4.5.4 – continued

with machined surfaces. The covers and frames shall be factory					coated with a smooth non-brittle coat of coal tar epoxy. Frames					and covers shall have an H-20 load rating.

500.4.5.5	Pipe sleeves shall be lock joint flexible sleeves which shall be cast				or locked into the manhole base. These sleeves shall be capable to 				allowing substantial off center alignment. The sleeves shall be 					attached securely to the outside of the pipe with stainless steel bands				to provide a water tight seal.

500.4.5.6	Manhole bases shall be installed before laying pipe to the manhole.				The manhole base shall be set on a 12” compacted stone bed. Once 				the sewer pipe has been connected to the manhole, barrel sections				shall be installed after installing kent seal at the joints. The pipe shall				extend into the manhole so that it is flush with the inside wall. There				shall be no pipe bells inside the manhole.

500.4.5.7	Manhole inverts shall be installed using bricks and mortar as shown on				the Contract Drawings. The trough and table shall be lined with 				bricks. The trough depth shall be equal to the pipe diameter. The tables				shall slope toward the trough at 1” per foot for drainage. The finished				surface of the invert shall be smooth, free of any obstructions and shall 			have a uniform pitch from inlet to outlet. The finish surface for both				inverts and tables shall be brick.

500.4.5.8	Install frames and covers as shown on the plans. The frames shall be				brought to the proper grade with brick and mortar or cast-in-place 				concrete. All voids between bricks shall be filled with mortar and the				bricks shall be coated with mortar on both the interior and exterior of				the manhole. The mortar surface shall be smooth and even and shall				slope inward on the exterior of the manhole to avoid lifting from frost.				Frames shall not be backfilled until the mortar has set and acquired 				sufficient strength to avoid damage. When manholes are in paved 				areas, the frame and cover shall be adjusted to grade once the base				pavement has been placed. The cost of adjusting the frame and cover 				to grade, including pavement cutting and replacement, is incidental to				the manhole cost. In paved areas the frame and cover shall be set ¼”				below final grade.

19

SECTION 500.0 – SEWER EXTENSIONS – continued

500.4.5.9	All manholes shall be vacuum tested immediately after assembly and 				prior to backfilling. All lift holes shall be plugged with an approved				non-shrink grout. All pipes entering the manhole shall be plugged. The				plugs shall be securely braced to prevent them from being sucked into				the manholes. The test head shall be placed at the inside of the top of				the cone section and seal inflated in accordance with the 					manufacturer’s recommendations. A vacuum of 10 inches of mercury				shall be drawn and the vacuum pump shut off. With the valves closed				the time shall be measured for a vacuum to drop to 9 inches. The test				shall pass if the time is greater than 60 seconds for 48” diameter, 75 				seconds for 60” and 90 seconds for 72” diameter manholes. If the				manhole fails the initial test, necessary repairs shall be made with a				non-shrink grout while the vacuum is still being drawn. Re-testing 				shall proceed until a satisfactory test is obtained.

500.5	All sewer mains shall be tested prior to acceptance. All testing shall be done in the presence of the Town. The Contractor shall notify the Town at least 48 hours in advance of any testing.

500.5.1	The Contractor shall only use testing equipment, plugs and 					compressors specifically designed for low pressure sewer testing. 				Equipment shall include a pressure relief valve set no higher than 9 				psig. The Contractor shall follow the manufacturer’s recommendation 				for operation and safety.  Equipment shall only be operated by 					personnel trained and experienced with its proper use.

For a sewer main test to be considered for acceptance, the sewer main				segment must be part of a manhole to manhole reach of pipe that has				been completed and backfilled to final grade. The manholes on each				end of the reach of pipe shall be successfully tested prior to testing of 				the sewer main.

The maximum allowable infiltration limit for all pipes shall be 100gal/				day/inch/mile of pipe installed. If there is evidence of poor workman-				ship, improper storage of pipe, or if test results are unsatisfactory, the				Engineer may direct that additional tests be made on any and all of the				pipe.

20

SECTION 500.0 – SEWER EXTENSIONS – continued

500.5 - continued

500.5.2	Test all gravity sewer lines for leakage by conducting a low pressure		 ex-filtration air test. All sewer lines shall be cleaned to remove all		 sediment and debris prior to testing.

Test plugs shall be properly installed and braced.

A minimum of 4 lbs/sq in air pressure shall be applied to the line				being tested. The air compressor shall then be shut off. A pressure				drop, from the applied pressure, of less than 1.0 psi during the period				of time specified in the table below will constitute an acceptable air				pressure test. If the pressure drop during the indicated time interval is				exceeded, the test will be determined as failure and the Contractor 				shall locate and correct the leak associated with failure. Following				correction of the leak the pipe shall be re-tested at the Contractor’s

expense.

Table of Air Test Durations

Sewer Diameter (Inches) 4 6 8 10 12 15 18 21 24-30

Test Duration (Minutes) 2 3 4 5 6 8 9 10 11.5

All sewer lines not complying with the requirements for infiltration 				and/or air testing shall be repaired or replaced at the Contractor’s				expense. The Contractor shall repair and re-test the line at his expense				until an acceptable test is achieved. No repairs will be made internally 				on the pipe unless specifically authorized by the Town in writing. All				repairs shall be made externally to the sewer lines. If any pipe is 				defective, it shall be removed and replaced.

If during the process of repairing the new sewer main or during other

operations not necessarily related to sewer construction (such as con-				structing roadways, cleanup, etc.), debris and sediment enters the new				sewer or manholes, the sewer shall again be cleaned before final 				acceptance shall be made.

500.5.3 	Prior to final acceptance of the sewer the Contract shall take deflection				measurements of all PVC sewer mains by use of a mandrel assembly 				(7 ½%) pilled through the entire length of each sewer run. If a 					deflection in the diameter of the pipe equal to or greater than 7 ½% of 				the specified pipe diameter is measured, the defective pipe will be 				removed and replaced by the Contractor at the Contractor’s expense. 				The pipe shall then be re-tested.

21

SECTION 500.0 – SEWER EXTENSIONS – continued

500.6	No builder or developer shall be issued a building permit for a new dwelling or

structure requiring sanitary facility within the Town, unless a suitable and approved method of sewage disposal is proposed. No certificate of occupancy	 shall be issued until connection is made to an approved sewer and all fees owed to the Town have been paid.

500.7	Connection of the sewer extension to the Town’s facilities shall not be permitted until: 1) the completed sewer has been tested and passed to the satisfaction of the

Town; 2) all fees have been paid to the Town; and 3) re-producible, mylar record

drawings of the completed sewer have been furnished to the Town. If developer desires to convey the sewer extension to the Town, he must give the Town a one year maintenance bond in an amount and form acceptable to the Town. In no event shall such bond be in an amount less than 10% of the cost of the extension. The Town shall in no event be required to accept an offer of conveyance of a sewer extension.

SECTION 600 – USE OF PUBLIC SEWERS

600.1	No person shall cause a connection to be made to a town sanitary sewer which shall discharge, or cause to be discharged, any storm water, surface water, ground water, roof runoff, subsurface drainage, un-contaminated cooling water, or un-polluted industrial process waters to any sanitary sewer. No direct connection shall be made from a public or private water supply to a building drain discharging to any sanitary sewer.

600.2	Storm water and all other un-polluted drainage may be discharged to such sewers as are specifically designated as storm sewers, or to a natural outlet approved by the Town. Industrial cooling water or un-polluted process waters may be discharged, on approval of the Town, to a storm sewer, or natural outlet, if in accordance with regulations of the Department of Environmental Protection.

600.3	Except as hereinafter provided, no person shall discharge or cause to be discharged, any of the following described waters or wastes to any public sewer:

600.3.1	Any liquid or vapor having a temperature higher than 150 degrees 				Fahrenheit (65 degrees Celsius).

600.3.2	Any waters or wastes which contain fats, grease or oil, or other sub-				stances in excess of 100mg/l, whether emulsified or not, that will 				solidify or become viscous at temperatures between 32 and 150 				degrees Fahrenheit.

22

SECTION 600 – USE OF PUBLIC SEWERS - continued

600.3 – continued

600.3.3	Any waters or wastes containing soluble fats, grease or oils, whether 				emulsified or not, exceeding an average 100 parts per million which, 				in the opinion of the Town, may overload or inhibit the Pollution 				Control Facility’s processes.

600.3.4	Any gasoline, benzene, naphtha, fuel oil, mineral oil, or other 					flammable or explosive liquid, solid or gas.

600.3.5	Any noxious or malodorous gas such as hydrogen sulfide, sulfur 				dioxide or nitrous oxide or other substance, which either singly or by				interaction with other wastes, are capable of creating public nuisance 				or hazard to life or of preventing entry into sewers for their					maintenance and repair.

600.3.6	Any garbage that has not been properly shredded. The installation and  			operation of any garbage grinder equipped with a motor of ¾ horse-				power or greater shall be subject to the  review and approval of the 				Town.

600.3.7	Any ashes, cinders, sand, mud, straw, shavings, metal, glass, rags, 				feathers, tar, plastic, cardboard, wood, paunch manure, hair and  				fleshings, entrails, lime slurry, lime residues, beer or distillery slops,				whey, chemical residues, paint residues, cannery waste, bulk solids, or				any other solid or  viscous substance capable to causing obstruction to				the flow of the sewers, or other interference with proper operation of 				the sewage works.

600.3.8	Any waters or wastes, acid and alkaline in reaction, having corrosive				properties capable of causing damage or hazard to structures, equip-				ment and personnel of the sewage works. Free acids and alkalis must 				be neutralized at all times, within a permissible pH range of 6.0 to 9.5.

600.3.9	Radioactive wastes or isotopes of half-life or concentrations as may 				exceed limits established by the Town in compliance with applicable				State or Federal regulations.

600.3.10	Quantities of flow, or concentrations of any wastewater constituent, or				both, which would constitute a “slug” as defined in Section 100.

23

SECTION 600 – USE OF PUBLIC SEWERS - continued

600.3 – continued

600.3.11	Any storm water, roof drains, spring water, cistern or tank overflow, 				footing drains, discharge from any vehicle wash rack or water motor,				or the contents of any privy vault, septic tank or cesspool, or the 				discharge of effluent from any air conditioning machine or refriger-				ation unit.

600.3.12	No person shall discharge or cause to be discharged any waters or 				wastes containing a toxic or poisonous substance, a high chlorine or 				oxygen  demand or suspended solids in sufficient quantity to injure or				interfere with any sewage treatment process, constitute a hazard to 				humans or animals, or create any hazard or violation in the receiving				waters or effluent of the Town’s sewage treatment plant, or 					contaminate or restrict the final end use of the treatment plant’s sludge				residuals. Such toxic substances shall be limited to the average con-				centrations listed hereinafter in the sewage as it leaves the building 				sewer and at no time shall the hourly concentration at the sewage 				treatment plant exceed three times the average concentration. If con-				centrations listed are exceeded, individual establishments will be sub-				ject to control by the Town in volume and concentration of wastes				discharged.

Limits of Toxic Substances in Sewage

Iron, as Fe							5.0  ppm

Chromium, as Cr (hexavalent)				1.0  ppm					Copper, as Cu					            1.0 ppm

Chlorine Demand					          15.0 ppm

Phenol							0.5 ppm

Cadmium, as Cd						0.5 ppm

Zinc, as Zn						0.5 ppm

Nickel							1.0 ppm

Mercury							0.2 ppm

The Town may periodically modify the above list of regulated toxic					substances and allowable concentrations in accordance with EPA					protocol for the development of technically based local limits. The 					Town will provide advanced written notice of new local limits to users					prior to initiating enforcement actions.

24

SECTION 600 – USE OF PUBLIC SEWERS - continued

600.3 – continued

600.3.13	Waters or wastes containing strong acid iron pickling wastes, or 					concentrated plating solutions, whether neutralized or not.

600.3.14	Waters or wastes containing phenols, or other taste or odor pro-						ducing substances, in such concentrations exceeding limits which					may be established by the Town as necessary, after treatment of the					composite sewage, to meet the requirements of the State, Federal, or					other public agencies of jurisdiction for such discharge to the 						receiving waters.

600.3.15	Waters or wastes containing substances which are not emenable to					treatment or reduction by the waste treatment processes employed, 					which may inhibit treatment plant processes or sludge quality or 					disposal, or are amenable to treatment only to such degree that the					sewage treatment plant effluent cannot meet the requirements of					other agencies having jurisdiction over the discharge to the receiving					waters.

600.3.16	Any heated waters or pollutants in amounts which will inhibit or 					interfere with biological activity in the Town’s waste water treatment					facilities, but in no case heated waters or pollutants in such quantities 					that the temperature at the Pollution Control Facility’s influent exceeds					104 degrees Fahrenheit (40 degrees Celsius).

600.3.17	Any waters or wastes containing color, dissolved solids, or dye which					would cause a visible discoloration of the treatment plant’s effluent 					or receiving water.

600.3.18	Any waters or wastes containing suspended solids, whether inert or 					organic, which would cause visible turbidity of the treatment plant’s					effluent or receiving water.

600.3.19	Any waters, wastes or substance which would cause the treatment 					plant’s effluent to exceed toxicity testing limits as may be required by					applicable State or Federal Law.

600.3.20 Any boiler blow offs or sediment trap wastes.

600.3.21	Any septage or septic process discharge without the express written 					approval of the Town.

25

SECTION 600 – USE OF PUBLIC SEWERS - continued

600.4	Any discharge of waters or wastes having a) a five (5) day Biochemical Oxygen 		Demand (BOD) greater than 300 parts per million; or b) containing more than 350		parts per million of suspended solids, or c) containing more than 15 parts per 		million of chlorine demand, or d) containing any quantity of substances having 		the characteristics described in this section or e) having an average daily flow or		pollutant mass greater than two (2) percent of the average daily sewage flow of 		the Town, shall be subject to the review and approval of the Town. Where 			necessary, in the opinion of the Town, the owner shall provide, at his expense,		such pre-treatment as may be necessary to, 1) reduce the Biochemical Oxygen		Demand to 300 parts per million and the suspended solids to 350 parts per million		by weight, or 2) reduce the chlorine demand to 15 parts per million, or 3) reduce 		objectionable characteristics or constituents to within the maximum limits pro-		vided for in this section, or 4) control the quantities and rates of discharge of such		waters or wastes. Plans, specifications, and any other pertinent information 		relating to proposed pre-treatment facilities shall be submitted for the approval of		the Town, and no construction of such facilities shall be commenced until said		approvals are obtained in writing. Failure to comply with one or more of the 		remedial procedures as required by the Town will constitute a violation of this 		Ordinance.

600.5	All measurements, tests, and analysis of the characteristics of waters and wastes 		to which reference is made in this Article shall be determined in accordance with		the latest accepted edition of the “Standard Methods for the Examination of Water		and Waste water”, upon suitable samples taken at a control manhole provided for		in Section 700. In the event that no manhole has been required, the manhole shall 		be considered to be the nearest downstream manhole in the public sewer from the		point at which the building sewer is connected.

600.6	No statement contained in this section shall be construed as preventing any 		special agreement or arrangement between the Town and any industrial concern		whereby an industrial waste of unusual strength or character may be accepted by 		the Town for treatment, subject to payment thereof by the industrial concern.

600.7	All of the preceding standards are to apply at the point where the industrial wastes		are discharged into the public sanitary sewerage system and any pre-treatment		required must be accomplished to practical completion before the wastes reach 		that point. The laboratory methods used in the examination of all industrial wastes		shall be those set forth in the latest accepted edition of “Standard Methods for the		Examination of Water and Sewage”. However, alternate methods for the analysis		of industrial wastes may be used subject to mutual agreement between the Town 		and the producer of such wastes. The frequency and duration of the sampling of

26

SECTION 600 – USE OF PUBLIC SEWERS - continued

600.7 - continued

any industrial waste shall not be less than once every three months for a twenty-		four (24) hour period. However, more frequent and longer periods may be 			required at the discretion of the Town.

600.8	If any waters or wastes are discharged, or are proposed to be discharged to 		the public sewers, which waters contain the substances or possess the 			characteristics enumerated in this section and which, in the judgment of the		Town, may have a deleterious effect upon the sewage works, processes, 		equipment or receiving waters, or which otherwise create a hazard to life or		constitute a public nuisance, the Town may:

600.8.1	Reject the wastes and require separate treatment

600.8.2	Require pre-treatment to an acceptable condition before dis-					charge to the public sewers.

600.8.3	Require control over the quantities and rates of discharge and/or

600.8.4	Require payment under the provisions of this Ordinance to cover 					the added cost of handling and treating of such wastes.

If the Town permits the pre-treatment or equalization of waste flows, the design and installation of plants and equipment shall be subject to the review and approval of the Town, and subject to the requirements of all applicable codes, Ordinances and laws, including Federal EPA pre-treatment standards.

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES

700.1	The Town, at its sole discretion, may elect to allow an industrial or unusual		waste producer to utilize the sewage works provided that it can be demon-		strated by the producer to the Town reasonable satisfaction that acceptance 		of the waste will result in:

700.1.1	No violation of applicable Federal or State regulations, including					EPA pre-treatment requirements.

700.1.2	No inhibition of, interference with, or damage to,  the treatment					plant’s processes or equipment and no upsets of the plant’s 						processes which lead to nuisance conditions,  operational problems					or discharge license non-compliance.

27

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.1 continued

700.1.3	No pass through of any waste material not treatable in the Town’s					treatment plant to the receiving waters.

700.1.4	No contamination of the Town’s sewage sludge with toxic or un-					desirable waste constituents and no impairment of the Town’s					ability to dispose of the treatment plant’s sludge residuals.

700.1.5	No creation of hazardous or unsafe conditions in the sewer system					or treatment plant which might jeopardize the health and welfare 					of the general public or the Town’s staff.

700.1.6	Equitable allocation of sewer user fees such that the true cost of 					treating the industrial or unusual waste is fully borne by the sewer					user that generated the wastes.

Prior to accepting the waste, the Town may require that appropriate industrial or unusual wastes undergo pre-treatment or flow equalization prior to its discharge into the Town’s sewer system.

700.2	Where pre-treatment or flow equalizing facilities are provided for any waters 	or wastes, they shall be maintained continuously in satisfactory and effective		operation by the owner, at his expense.

700.3	When required by the Town, the owner of any property served by a building		sewer carrying industrial wastes shall install a suitable control structure in 		the building sewer to facilitate observation, sampling, and measurement of 		the wastes. Such manhole, when required, shall be accessible and safely		located and shall be constructed in accordance with plans approved by the		Town. The manhole shall be installed by the owner at his expense, and shall		be maintained by him so as to be safe and accessible at all times.

700.4	No discharge or user shall increase the use of potable or process water, in 		any way, for the purpose of diluting a discharge as a partial or complete sub-		statute for adequate treatment to achieve compliance with the standards set		forth in this Ordinance. Pollutants, substances or waste water prohibited by 		this Ordinance shall not be processed or stored in a manner that would allow		them to be discharged to the treatment plant.

28

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.5	Grease, oil, and sand interceptors shall be provided by the producer when 		the Ordinance limits for those substances are exceeded or when, in the 		opinion of the Town, they are necessary for the proper handling of wastes		containing grease in excessive amounts, or any flammable wastes, sand or 		other harmful ingredients; except that such interceptors shall not be re-		quired for private living quarters or dwelling units. All interceptors shall be		of a type and capacity required by the State of Maine Plumbing Code and		as required for sub-surface waste water disposal systems and shall be 			approved by the Town prior to installation, and shall be located as to be 		readily and easily accessible for cleaning and inspection.

Grease and oil interceptors shall be constructed of impervious materials 		capable of withstanding abrupt and extreme changes in temperatures. They		shall be of substantial construction, water tight, and equipped with easily		removable covers which, when bolted in place, shall be gas tight and water 		tight.

700.6	Where installed, all grease, oil and sand interceptors shall be maintained by		the owner, at his expense, in continuously efficient operation at all times and		shall be readily accessible and open to inspection by the Town at any time. A		maintenance record shall by maintained by the owner for the Town’s 			periodic review.

700.7	The categorical pre-treatment standards found at 40 CFR Chapter I, Sub-		chapter N, Parts 405-471 and as from time to time amended are incorporated		herein by reference. These standards must be adhered to by dischargers to, 		or users of, the Town’s sewage works.

700.8	Local limits for certain pollutants may be established by the Town to protect		against pass through, interference, process inhibition and damage, safety 		concerns, and sludge residual contamination. No person shall discharge 		waste water containing in excess of the instantaneous maximum allowable		discharge limits as identified in this Ordinance or on the user’s waste water		discharge permit. All discharge limits shall be technically based and 			approved by the appropriate regulatory agencies.

700.9	When requested by the Town, users must complete a waste water survey 		form, on a form, supplied by the Town, which contains information on the		nature and characteristics of their wastes. This form must be submitted to 		the Town prior to the discharge of the user’s waste water into the Town’s

29

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.9 – continued

sewage works. The Town is authorized to prepare a form for this purpose		and may periodically require users to update the survey. Failure to complete		this waste water survey form shall be reasonable	grounds for terminating		service to the user and shall be considered a violation of this Ordinance. 		Existing industrial dischargers shall file waste water survey forms within		thirty (30) days after being notified by the Town, and proposed new dis-		chargers shall file such forms at least ninety (90) days prior to connecting		to the sewage works. The form shall include, but not be limited to, the			following information:

700.9.1	The name, address, and location of the user and the number of					employees.

700.9.2	The Standard Industrial Classification (SIC) Code of the user.

700.9.3	The known, or suspected to be present, waste water constituents					and characteristics, including, but not limited to, those listed in 					this Ordinance. Any sampling and analysis that is required by the					Town shall be performed in accordance with Standard Methods.					The costs of all such sampling, analysis, and reporting shall be 					fully borne by the user.

700.9.4	The time and duration of discharges.

700.9.5	The average daily and instantaneous peak waste water flow rates,					in gallons per day, including daily, monthly and seasonal 						variations, if any. All flows shall be as actually measured unless					other verifiable measurement techniques are approved by the 					Town.

700.9.6	The site plans, floor plans, mechanical and plumbing plans and					details to show all sewers, sewer connections, inspection manholes,					sampling chambers and appurtenances by size, location, and ele-					vation adjacent to, or at, the user’s premises.

700.9.7	The activities, facilities, and plant processes on the premises, 					including all materials which are, or may be, discharged to the					sewage works.

30

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.9 – continued

700.9.8	The nature and concentration of any known or suspected 						pollutants or materials prohibited by this Ordinance from being					included in the discharge, together with a statement regarding 					whether or not compliance is being, or will be achieved with this					Ordinance on a consistent basis and if not, whether additional					operations and maintenance activities and/or additional pre-					treatment is required for the user to comply with this Ordinance.

700.9.9	The identification of each product produced by the user by type,					amount, process or processes, and rate of production.

700.9.10	The type and amount of raw materials utilized, average and						maximum per day, by the user.

700.10	All disclosure forms and any periodic reports submitted by a user shall be

signed by the principal executive officer of the user and  shall contain the	 following certification: “I certify under penalty of law that this document and all attachments were prepared under my direction or supervision in	 accordance with a system designed to assure that qualified personnel 		 properly gather and evaluate the information submitted. Based on my 	 inquiry of the persons who manage the system, or those persons directly	 responsible for gathering the information, the information submitted is, to	 the best of my knowledge and belief, true, accurate, and complete. I am aware that there are significant penalties for submitting false information, 	 including the possibility of fine and imprisonment for knowing violations.”

700.11	The Town will evaluate the completed waste water survey forms and material safety data furnished by the user and may require the user to furnish additional information. The user shall provide all requested 		 additional information within fifteen (15) days after receiving notification	 from the Town that additional information is required. After full evaluation	 and acceptance of all submitted data, the Town shall make the determination	 as to whether the user is subject to pre-treatment requirements. If the Town   determines that the user is subject to pre-treatment requirements, the Town 	 shall require the user to apply for a Wastewater Discharge Permit as required by this Section 700.  The user shall make application for a Wastewater Discharge Permit, on a form provided by the Town, within	 thirty (30) days after having received notification from the Town to do so. The user shall provide with the permit application, at the user’s own expense,

31

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.11 – continued

the results of all sampling and analysis of the user’s waste water effluent as 		the Town may require to accompany the permit application. If so requested		by the Town, the user shall collect all required samples in the presence of the		Town.

700.12	Every new or existing user of the Town’s sewage works who is determined to		be a categorical user or significant industrial user as defined in Section 100 of 	this Ordinance is required to obtain a waste water discharge permit from the		Town.

700.13	Wastewater discharge permits shall include such conditions as are 			reasonably deemed necessary by the Town to prevent waste pass through or 		interference, protect the quality of the water body receiving the Treatment 		Plant’s effluent, protect worker health and safety, facilitate sludge manage-		ment and disposal,  and protect against damage to the sewage works. Waste		water discharged permits may impose effluent restrictions or limits on the		user if the Town determines that such limits are necessary to protect the 		quality of the Treatment Plant influent, effluent, or sludge, or to maintain		compliance with any applicable Federal or State law, including requirements		under the Town’s NPDES permit and national categorical pre-treatment		standards for new and existing sources set forth in 40 CFR Chapter I,  		Subchapter N Parts 401-471.

700.14	Wastewater discharge permits shall be issued for a specified time period, not		to exceed five (5) years. A wastewater discharge permit may be issued for a		period of less than five (5) years. Each wastewater discharge permit shall 		indicate a specific date upon which it will expire and no permit shall run 		beyond the expiration of the Town’s NPDES permit. Such discharge permit		may, after written notice and hearings be suspended or revoked by the Town 		Selectmen for violation of the permit or change of law applicable to the 		subject matter of the permit.

700.15	Wastewater discharge permits shall be issued to a specific operation. A 		wastewater discharge permit shall not be re-assigned or transferred or sold 		to a new owner or a new user, different premises, or a new or changed 		operation. To facilitate the issuance of new, separate permits, the Town may		allow new owners or individuals to operate under an existing wastewater 		discharge permit for a period not to exceed ninety (90) days.

32

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.16	Wastewater discharge permits may contain requirements and compliance 		schedules for the installation of pre-treatment technology, pollution control,		or construction of appropriate containment devices, any of which would be		designed to reduce, eliminate, or prevent the introduction of pollutants into		the Town’s sewage works.

700.17	Wastewater discharge permits may contain requirements for the develop-		ment and implementation of spill control plans or other special conditions		including management practices necessary to adequately prevent accidental,		unanticipated, or routine discharges to the Town’s sewage works.

700.18	Wastewater discharge permits may contain requirements for the installation		and maintenance of inspection and sampling facilities and equipment and for 	the reporting of all results to the Town.

700.19	The Town, for good cause, may at any time, modify any wastewater dis-		charge permit so long as the public health and safety are maintained.

700.20	Seven days advance written notice of intent to revoke and an opportunity for		hearing before the Town Selectmen shall be provided before revocation of		any permit for a violation of any condition thereof or of this Ordinance, 		significant non-compliance, or any applicable State or Federal Statutes, 		rules, or regulations.

700.21	The Town may require any user to develop and implement an accidental		hazardous waste discharge/slug control plan. At least once every two (2) 		years, the Town shall evaluate whether each significant industrial user needs		such a plan. Any user required to develop and implement an accidental		hazardous waste discharge/slug control plan shall submit a plan which 		addresses, at a minimum, the following:

700.21.1	Description of discharge practices, including non-routine batch					discharges;

700.21.2	Description of stored chemicals;

700.21.3	Procedures for immediately notifying the Town of any accidental					or slug discharge. Such notification must also be given for any

33

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.21.3 - continued

accidental or slug discharge. Such notification must also be given					for any discharge which would violate any of the prohibited 					discharges in this Ordinance; and

700.21.4	Procedures to prevent adverse sewage works impacts from any					accidental or slug discharge. Such procedures include, but are not					limited to, inspection and maintenance of storage areas, handling					and transfer of materials, loading and unloading operations, 					control of plant site runoff, worker training, building of contain-					ment structures or equipment, measures for containing toxic 					organic pollutants (including solvents), and/or measures and 					equipment for emergency response.

700.21.5	Procedures for notifying the Plant Operator of Hazardous waste					discharges.

700.22	Where additional pre-treatment and/or operations or maintenance activities	   	will be required to comply with this Ordinance, the user shall provide a 	  	declaration of the shortest schedule by which the user will provide such 		additional pre-treatment and/or implementation of additional operations and		maintenance activities. The Town reserves the right to determine the reason-		ableness of the proposed schedule, to modify the proposed schedule, or to 		reject the schedule. The schedule shall contain milestone dates for the 			commencement and completion of major events leading to the construction 		and operation of additional treatment required for the user to comply with 		the requirements of this Ordinance, including, but not limited to, dates		relating to hiring an engineer, completing preliminary plans, completing 		final plans, executing contracts for major components, commencing 	construction, completing construction, and all other acts necessary to achieve		compliance with this Ordinance. No later than fourteen (14) days following 		each milestone date in the schedule and the final date for compliance, the 		user shall submit a progress report to the Town including, at a minimum, a		statement as to whether or not it complied with the increment of progress		represented by that milestone date and, if not, the date on which it expects		to comply with this increment of progress, the reason for delay, and the steps		being taken by the user to return to the approved schedule.

700.23	All significant industrial user(s) shall, at a frequency stated in their waste-		water permit or as determined by the Town, but in no case less than twice 		per year, submit a report to the Town indicating the nature and

34

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.23 – continued

Concentration of pollutants in the discharge which are limited by pre-			treatment permit criteria or Ordinance standards and the measured or 		estimated average and maximum daily flows and loadings for the reporting		period. All periodic compliance reports must be signed and certified in		accordance with this Ordinance. All wastewater samples collected must be		representative of the user’s discharge. Wastewater monitoring and flow 		measurement facilities shall be properly operated, kept clean and maintained		in good working order at all times. The failure of a user to keep its			monitoring facility in good working order shall not be grounds for the user to 	claim that sample results are unrepresentative of its discharge. If a user 		subject to the reporting requirement in this Ordinance or its permit monitors		any pollutant more frequently than required, the results of this additional		monitoring shall be included in the report.

700.24	Each user must notify the Town in writing of any planned significant 			changes to its operations or process systems which might alter the nature, 		quality or volume of its wastewater at least sixty (60) days before the change.  	No user shall implement the planned changed condition(s) until and unless 		the Town has responded in writing to the user’s notice. Significant changes		include, but are not limited to, flow or pollutant load increases of ten percent 		(10%) or greater, and the discharge of any previously unreported pollutants.

700.25	If sampling performed by a user indicates a violation of their permit or this		Ordinance, the user must notify the Town within twenty-four (24) hours of		becoming aware of the violation. The user shall also within five (5) calendar		days repeat the sampling and analysis and submit the results of the repeat		analysis to the Superintendent within five (5) calendar days of such repeat	sampling and analysis. In the case of any discharge, including, but not			limited to, hazardous waste discharges, accidental discharges, discharges of a		non-routine or episodic nature, a non-customary batch discharge, or a slug		load that may cause potential problems for the sewage works, the user shall		immediately telephone and notify the Town of the incident. This notification		shall include the location of the discharge, type of waste, concentration and 		volume, if known, and corrective actions taken by the user. Within five (5)

Days following such a discharge, the user shall submit a detailed written 		report describing the cause(s) of the discharge and the measures to be taken		by the user to prevent similar future occurrences. Such notification shall not		relieve the user of any expense, loss, damage, or other liability which may be		incurred as a result of damage to the sewage works, natural resources or

35

SECTION 700.0 – PRE-TREATMENT AND PERMITTING OF INDUSTRIAL                      AND UNUSUAL WASTES – continued

700.25 – continued

Other damage to person or property; nor shall such notification relieve the 		user of any fines, penalties or other liability which may be imposed pursuant 		to this Ordinance. A notice shall be permanently posted on the user’s bulletin		board or other prominent place advising employees whom to call in the event 	of a discharge described above. Employers shall ensure that all employees, 		who may cause such a discharge to occur, are advised of the emergency 		notification procedure.

SECTION 800.0 – ORDINANCE COMPLIANCE MONITORING

800.1	In accordance with 30-A M.R.S.A., Section 4213, the Machias Plumbing		Inspector may enter any property at reasonable hours for the purpose of		inspecting the property for compliance with applicable rules or to investigate		alleged conditions which do not comply with the rules. This Right of Entry 		extends to the right to enter any building with the consent of the property		owner, occupant or agent. Upon the request of the occupant of the premises,		the Plumbing Inspector shall present proper credentials before entering the		premises.

If entry is denied, before attempting entry, the Plumbing Inspector must 		obtain an Administrative Inspection Warrant from the District Court,			pursuant to the procedures set out in detail in Rule 80E, Maine Rules of Civil		Procedure.

800.2	The Town and other duly authorized employees of the Town bearing proper		credentials and identification shall be permitted to enter all private 			properties through which the Town holds an easement for the purposes of, 		but not limited to, inspection, observation, measurement, sampling, repair 		and maintenance of any portion of the sewage works lying within said 			easement. All entry and subsequent work, if any, on said easement, shall be		done in full accordance with the terms of the easement pertaining to the		private property involved.

800.3	The Town shall have authority to set up, on the user’s property, or require		installation of, such devices as are necessary to conduct sampling and/or		metering of the user’s waste discharges. The user shall bear the costs of such

setup or installation.

36

SECTION 800.0 – ORDINANCE COMPLIANCE MONITORING – continued

800.4	The Town shall require the user to install monitoring equipment as the Town 	deems necessary. The user’s sampling and monitoring equipment shall be		maintained at all times in a safe and proper operating condition by the user		at its own expense. All devices used to measure wastewater flow and quality		shall be calibrated at least quarterly to ensure their accuracy.

800.5	Users subject to the reporting requirements of this Ordinance shall retain, 		and make available for inspection and copying, all records or information		obtained pursuant to any monitoring activities required by Ordinance and 		any additional records or information obtained pursuant to monitoring		activities undertaken by the user independent of such requirements. Records		shall include, but not be limited to the date, exact place, method, and time of		sampling and the name of the person(s) taking the samples; the dates 			analysis were performed; who performed the analyses; the analytical 			techniques or methods used; and the results of such analyses. These records		shall be retained by the user for a period of at least three (3) years. This 		period shall be automatically extended for the duration of any litigation		concerning the user or the Town, or where the user has been specifically		notified of a longer retention period by the Town.

800.6	Information and data on a user obtained from reports, surveys,  wastewater		discharge permits and monitoring programs, and monitoring programs, and		from the  Town’s inspection and sampling activities, shall be available to the		public without restriction, unless the user specifically requests, and is able to		demonstrate to the satisfaction of the Town, that the release of such 			information would divulge information, processes or methods of production		entitled to protection as trade secrets or proprietary information on the user		which under applicable State law is not subject to public inspection. When		requested and demonstrated by the user furnishing a report that such			information must be held confidential under State law, the portions of a 		report which might disclose such confidential information shall not be made		available for inspection by the public, but shall be made available 			immediately, upon request, to State and Federal governmental agencies for 		uses related to the NPDES program or pre-treatment program, and in			enforcement proceedings involving the person furnishing the report. 			Wastewater constituents and characteristics and other “effluent data” as 		defined by 40 CFR Part 2.032 will not be recognized as confidential 			information and will be available to the public without restriction.

37

SECTION 800.0 – ORDINANCE COMPLIANCE MONITORING – continued

800.7	If the Town has been refused access to any building, structure or property, 		or any part thereof, for the purpose of inspecting, sampling or otherwise		monitoring compliance with this Ordinance, the Town shall seek to secure		an Administrative Inspection Warrant pursuant to M.R. Civ.P. 80E. The		warrant, if issued by the District Court, shall be executed pursuant to			M.R.Civ.P. 80E and the Town shall be accompanied by a uniformed Town 		police officer during said execution.

SECTION 900.0 – PROTECTION FROM DAMAGE

900.1	No person shall maliciously, willfully, or negligently break, damage, destroy,		uncover, deface or tamper with any structure, appurtenances or equipment		which is a part of the sewage works. Any person violating this provision shall		be subject to prosecution criminally or civilly or both.

900.2	Before a permit will be issued for construction of building sewers, or sewer, or		sewer extensions, pump stations and/or treatment structures (except on private		property), the construction contractor must present a certificate of insurance 		showing minimum liability coverage of $1,000,000/$2,000,000 for bodily injury		and a $100,000 limit for property damage including collapse and underground		coverage.

SECTION 1000.0 – SEWER CHARGES

1000.1	The source of a portion of the revenues for retiring debt services and for capital		expenditures, operation and maintenance of the sewage works shall be a Sewer		Service Charge. That portion of the Sewer Service Charge related to capital 		expenditures and retirement of debt service shall be made against all properties		within the Sewage  Works service area having or required to have sanitary 		facilities, whether actually connected to the public sewer system or not. The		Sewage Works service area and the nature of buildings required to have sanitary		facilities shall be as defined as Section 200.4 hereof. In the case of a building not		connected to the Sewage Works, such charge shall be deemed by “ready to serve”		charge levied to aid in defraying expense incurred in making service available to		the property. In the case of a connected building not in active use or occupancy 		and having no discharge during a given billing period, the portion related to 		capital expenditures and retirement of debt services shall be regarded as a 			minimum charge. In the case of a connected building actively discharging to the		Sewage Works for all or part of any given billing period, the charge shall be 		increased to include the cost of operations and maintenance of the Sewage Works.

38

SECTION 1000.0 – SEWER CHARGES – continued

1000.2	The Board of Selectmen shall establish sewage charges for the connection to and		use of public sewerage facilities to be paid by every owner (of an establishment)		whose building sewer connects directly or indirectly into public sewers. Such 		sewage charges shall be in proportion to the quantity of water supplied to every		such premise, subject to just and equitable discounts and abatements in			exceptional cases.

1000.3	A special sewage service charge shall be established by the Town for any 			industrial firm or organization who, by virtue of the volume, strength or unusual		characteristic of their waste alone, would overload or upset the capacity of 		efficiency of the sewerage works or any part thereof if such waste entered the 		public sewer, or whose waste disposal situation is such that it would be in the 		public interest to waive the basic requirements. The Board of Selectmen, after		appropriate study, may from time to time establish a Special Sewer Service 		Charge to such industrial firm by separate agreement with said firm. The 			applicable portions of the proceeding Sections, as well as the equitable rights of		the public shall be the basis for such an arrangement. No such special sewer 		charge shall extend for more than two (2) years and such charges may be 			modified due to material charges of law, charges of operating costs, or other		reasonable circumstances which make the initial sewer charge unfair or			inequitable in the view of the Machias Board of Selectmen.

1000.4	An interest charge at the same rate as established by the Board of Selectmen for 		uncollected taxes will be made on all bills not paid prior to the due date of 			invoice.

SECTION 1100.0 – ENFORCEMENT

1100.1	Nuisances and violation of this ordinance shall be deemed to be a nuisance and a		land use violation under rule 80K and 30-A MRSA, Section 4452.

1100.2	Enforcement:  If the Town shall find that any provision of this Ordinance is being 		violated, notification in writing will be sent to the person responsible for such		violation, indicating the nature of the violation and ordering the action necessary		to correct it, including discontinuance of illegal use of the Municipal Sewer 		System, and abatement of nuisance condition. A copy of such notices shall be 		maintained as a permanent record.

39

SECTION 1100.0 – ENFORCEMENT – continued

1100.3	Legal Action:  When the above action does not result in the correction or 			abatement of the violation or nuisance condition, the Selectmen, after notice		from the appropriate Town official, is hereby authorized to direct the Town 		Attorney to institute any and all actions and  proceedings, either legal or 			equitable, including actions seeking injunctions of violations and the imposing 		of fines, that may be available or necessary to enforce the provisions of this		ordinance in the name of the Town.

1100.4	Penalty:  Any person, including, but not limited to a landowner, a landowner’s		agent or a contractor, who violates any provision of this Ordinance shall be 		penalized in accordance with 30-A, MRSA Section 4452 as now existing or 		subsequently amended.

In addition, the Town Of Machias shall be entitled to all of the relief, including		its costs and legal fees as allowed by said Section 4452. Notwithstanding any		provision to the contrary, including the Provision of 30-A M.R.S.A. Section 4452, 	as now existing or amended in the future, the Town Of Machias shall be entitled		to judgment against any violator for its costs, expert witness fees, code			enforcement expenses and attorneys’ fees incurred in enforcing this Ordinance. 		The Town Of Machias shall also have the right to enforce this Ordinance through		civil action, either at law or equity. The enforcement provisions herein contained		shall exist in addition to those which may exist under Maine Statutory law or 		Maine Rule or Civil Procedure 80K, or any other court rule or statutory provision.

Each and every day of violation shall constitute a new and separate offenses for 		which a minimum penalty of $100.00 shall be assessed.

SECTION 1200.0 – CONFLICT WITH OTHER ORDINANCES AND DOCUMENTS

1200.0	Unless specified herein, this Ordinance does not repeal any other law, ordinance,		regulation, rule, code or otherwise lawful deed restriction or covenant. Whenever		the requirements of this ordinance are at variance with the regulations or 			restrictions of any other lawfully adopted law, ordinance, rule or regulation 		imposed by any governmental authority or any deed restriction or covenant, that		which is more restrictive or imposes the higher standards or requirements shall		govern. Not withstanding any other provisions of this Ordinance no premises shall		be used or maintained in violation of any State or Federal pollution control or		environmental protection law or regulation.

40

SECTION 1300.0 – SEVERABILITY

1300.0	In the event that any section, subsection or any portion of this Ordinance shall be 		declared by any Court of competent jurisdiction to be invalid for any reason, such		decision shall not be deemed to affect the validity of any other section, subsection		or other portion of this Ordinance. To this end, the provisions of the Ordinance 		are hereby declared to be several.

This Ordinance received its final reading on ____________________ and was passed by

Unanimous vote at that time and shall be in full force and effect upon being published in full force and effect upon being published in full within ten days after its final passage.

Attest:_______________________________________

Town Clerk

41

Example

TOWN OF MACHIAS WWTF

Technical Based Limits for Industrial Discharges in the Town of Machias

METHOD – Allowable Headworks Loadings Based on Prevention of Pollutant Pass				      Through for BOD and TSS.

(8.34) (30mg/l average permitted NPDES discharge limit at Sewage Works) (0.37MGD)

15 percent of pollutants left in discharge

= 617 pounds of BOD and TSS that SewageWorks can technically treat daily

Domestic and commercial contributions = BOD – 500 pounds/day; TSS – 400 pounds/day

Allowable Industrial contributions = BOD – 617 allowable – 500 actual = 117 pounds/day

TSS – 617 allowable – 400 actual = 217 pounds/day

Machias Wastewater Sewer Connection and Dumping Fees

The Machias Board of Selectmen hereby establishes the following rates to be charged for

The Machias Wastewater Sewer Connection Fees and Dumping Fees in accordance with the Machias Sewer Ordinance. Said fees will become effective on April 1, 2006 and become a part of said Ordinance.

*Changes made to Resident and Non-resident Dumping Fees as of January 23, 2008.

Sewer Line Reconnection Fee:	$ 10.00 Per Unit For Residential

Sewer Line Reconnection Fee:	$ 50.00 Per Unit For Commercial

New Sewer Line Connection Fee:	$ 50.00 Per Unit For Residential

New Sewer Line Connection Fee:	$300.00 Per Unit For Commercial

R. V. Dumping Fee:	$ 10.00 Per R.V.

Resident Dumping Fee:	$ 50.00 Per Thousand Gallons*

Non-Resident Dumping Fee:	$125.00 Per Thousand Gallons*

All connections to the Machias Wastewater Sewer System shall require an approved permit be obtained and the submission of required fees in advance of any work being performed. Please review the Machias Sewer Ordinance for additional information and  requirements.

MACHIAS BOARD OF SELECTMEN

________________________________               _______________________________

________________________________               _______________________________

________________________________              Dated:__________________________

TOWN OF MACHIAS

SEWER RATES 2010

TO BE EFFECTIVE JANUARY 1, 2010

CUBIC FEET                      DEBT SERVICE          OPERATION/MAINT     	TOTAL

000 -1000		$16.72	$45.00	$ 61.72

1001-1100			4.50	   66.22

1101-1200			4.50	   70.72

1201-1300			4.50	   75.22

1301-1400			4.50	   79.72

1401-1500			4.50	   84.22

1501-1600			4.50	   88.72

1601-	1700			4.50	   93.22			1701-1800			4.50	   97.72

1801-1900			4.50	 102.22

1901-2000			4.50	 106.72

2001-2100			4.50	 111.22

2101-2200			4.50	 115.72			2201-2300			4.50	 120.22			2301-2400			4.50	 124.72

2401-2500			4.50	 129.22			2501-2600			4.50	 133.72

2601-2700			4.50	 138.22			2701-2800			4.50	 142.72			2801-2900			4.50	 147.22			2901-3000			4.50	 151.72

3001-3100	                 additional 16.72	4.50	 172.94

3101-3200			4.50	 177.44

3201-3300			4.50	 181.94

For each additional 100 cubic feet add $4.50

For each additional 3000 cubic feet increment add $16.72 for Debt Service

Water Supply other than Machias Water Company or not metered = $111.22